## Asset Schedule Intro
Asset Schedule Data Requirements
Asset Schedule Data Requirements | All maintainable assets should be defined as separate line items in the appropriate MEP schedule. Each asset requires the following fields: (1) Schedule Tag - see below the 'Schedule Tag Methodology'. Refer to the 'Asset Schedule Tag' sheet for abbreviations. (2) Location - the location/room where the asset/equipment is physically installed. This field must reference the official room/location number as approved by Caltech. (3) Location Served - the location/room that the asset/equipment serves. This field must reference the official room/location number as approved by Caltech unless mutiple rooms are served. In this case, refer to floor/suite/lab, etc. (4) Served By - if the asset/equipment is served by another asset (e.g. VAV is served by the AHU), then refer to the schedule tag of the parent asset here.
Schedule Tag Methodology | The convention for creating schedule tags shown below should be used across all project plans, drawings, submittals, BAS controller object, Niagara point folders, etc. Refer to the 'Asset Schedule Tag' sheet for actual schedule tag abbreviations. Schedule Tag Abbrreviation - Floor# - Unique Sequential Number For example: AHU-R-1, AHU-R-2, AHU-B2-1, VVS-B2-1, VVS-B2-2, VVS-B1-1, VVS-B1-1 The 'Unique Sequential Number' is unique only within a given building-floor and schedule tag abbreviation combination. Floor #s are generally: B2,B1,1,2,3,4,R (roof), P (penthouse)

## Asset Schedule Tags
Schedule Tag Example | Keyword Name | Asset Major Group Description | QR Sticker | Caltech Internal Only
DUM-1-1 | DUMBWAITER | Conveying Systems and Material Handling Products | Metal Dogtag | false
ELEV-1-1 | ELEVATOR | Conveying Systems and Material Handling Products | Metal Dogtag | false
HANDI-1-1 | HANDICAP LIFT | Conveying Systems and Material Handling Products | Metal Dogtag | false
DATA-1-1 | DATA SYSTEM | Electrical and Lighting Specific Products and Equipment | None | true
DC SYS-1-1 | DC POWER CONTROL SYSTEM | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | true
DISTP-1-1 | ELECTRICAL DISTRIBUTION PANEL | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
DIST SYS-1-1 | ELECTRICAL DISTRIBUTION SYSTEM | Electrical and Lighting Specific Products and Equipment | None | true
EMG CR-1-1 | EMERGENCY CIRCUIT | Electrical and Lighting Specific Products and Equipment | None | false
EMG EX-1-1 | EMERGENCY EXIT | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
EMG LTG-1-1 | EMERGENCY LIGHT | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
EGR-1-1 | EMERGENCY LIGHT AND EXIT SIGN COMBO | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
EXLTG SYS-1 | EXTERIOR LIGHTING SYSTEM | Electrical and Lighting Specific Products and Equipment | None | true
FCELL-1-1 | FUEL CELL | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
DISC-1-1 | FUSED DISCONNECT | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
INTLTG SYS-1-1 | INTERIOR LIGHTING SYSTEM | Electrical and Lighting Specific Products and Equipment | None | true
LTGC-1-1 | LIGHTING CONTROLS | Electrical and Lighting Specific Products and Equipment | None | false
CRB-1-1 | LOW VOLTAGE CIRCUIT BREAKER | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
LVD-1-1 | LOW VOLTAGE DISCONNECT | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
CRB-1-1 | MEDIUM VOLTAGE CIRCUIT BREAKER | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
MVD-1-1 | MEDIUM VOLTAGE DISCONNECT | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
SPL-1-1 | MEDIUM VOLTAGE SPLICE BOX | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
TAP-1-1 | MEDIUM VOLTAGE TAP FEEDER | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
MCC-1-1 | MOTOR CONTROL CENTER | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
SF6-1-1 | SF6 SWITCH | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
INV-1-1 | STANDBY POWER INVERTER | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
STRTR-1-1 | STARTER | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
VFD-B1-1 | VARIABLE FREQUENCY DRIVE | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
PB-1-1 | PANELBOARD | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
TF-1-1 | TRANSFORMER | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
GEN-1-1 | STANDBY POWER GENERATOR | Electrical and Lighting Specific Products and Equipment | Metal Dogtag | false
ATS-1-1 | AUTOMATIC TRANSFER SWITCH | Electrical and Lighting Specific Products and Equipment | Vinyl Sticker | false
BBP-1-1 | BLOODBORNE PATHOGEN KIT | Facility and Occupant Protection Products | Vinyl Sticker | false
BSCR SYS-1 | BUILDING SECURITY SYSTEM | Facility and Occupant Protection Products | None | true
EMG LTG SYS-1-1 | EMERGENCY EXIT AND LIGHT SYSTEM | Facility and Occupant Protection Products | None | true
EMG PH-1-1 | EMERGENCY PHONE | Facility and Occupant Protection Products | Vinyl Sticker | false
FIRE SYS-1-1 | FIRE SYSTEM | Facility and Occupant Protection Products | None | true
FEXT SYS-1-1 | PORTABLE AED AND FIRE EXTINGUISHER SYSTEM | Facility and Occupant Protection Products | None | true
HARN-1-1 | SAFETY HARNESS | Facility and Occupant Protection Products | Metal Dogtag | false
AED-1-1 | AED | Facility and Occupant Protection Products | Vinyl Sticker | false
CRDR-1-1 | CARD READER DOOR | Facility and Occupant Protection Products | None | false
FEXT-1-1 | FIRE EXTINGUISHER | Facility and Occupant Protection Products | Vinyl Sticker | false
CARP-1-1 | CARPENTRY EQUIPMENT | Furnishings, Fixtures and Equipment Products | None | false
CURT-1-1 | AIR CURTAIN | Furnishings, Fixtures and Equipment Products | Vinyl Sticker | false
CHAR-1-1 | CHARBOILER | Furnishings, Fixtures and Equipment Products | None | false
DWSH-1-1 | DISHWASHER | Furnishings, Fixtures and Equipment Products | None | false
DUMP-1-1 | DUMP STATION | Furnishings, Fixtures and Equipment Products | None | false
FRY-1-1 | FRYER | Furnishings, Fixtures and Equipment Products | None | false
GRID-1-1 | GRIDDLE | Furnishings, Fixtures and Equipment Products | None | false
HHLD-1-1 | HOT HOLDING CABINET | Furnishings, Fixtures and Equipment Products | None | false
ICE-1-1 | ICE MACHINE | Furnishings, Fixtures and Equipment Products | None | false
KH-1-1 | KITCHEN EXHAUST HOOD | Furnishings, Fixtures and Equipment Products | None | false
KHCP-1-1 | KITCHEN HOOD CONTROL PANEL | Furnishings, Fixtures and Equipment Products | None | false
KVENT-1-1 | KITCHEN VENTILATION DUCT | Furnishings, Fixtures and Equipment Products | None | false
OVEN-1-1 | OVEN | Furnishings, Fixtures and Equipment Products | None | false
RFRG-1-1 | REFRIGERATOR | Furnishings, Fixtures and Equipment Products | None | false
PULL-1-1 | REMOTE PULL STATION | Furnishings, Fixtures and Equipment Products | None | false
SOFT-1-1 | SOFT SERVE | Furnishings, Fixtures and Equipment Products | None | false
FPNL-1-1 | FIRE PANEL | General Facility Services Products | None | false
SPRNK-1-1 | FIRE SPRINKLER SYSTEM | General Facility Services Products | None | true
FSUPR-1-1 | FIRE SUPPRESSION SYSTEM | General Facility Services Products | None | true
FMTR-B1-1 | FAN MOTOR | General Facility Services Products | Vinyl Sticker | false
MTR-1-1 | MOTOR | General Facility Services Products | Vinyl Sticker | false
PMTR-B1-1 | PUMP MOTOR | General Facility Services Products | Vinyl Sticker | false
ACB-1-1 | ACTIVE CHILLED BEAM | HVAC Specific Products and Equipment | None | false
DRYR-1-1 | AIR DRYER | HVAC Specific Products and Equipment | Metal Dogtag | false
ARVR-1-1 | AIR RECEIVER | HVAC Specific Products and Equipment | Metal Dogtag | false
ACTY SYS-1-1 | AIRCUITY SYSTEM | HVAC Specific Products and Equipment | None | false
EAF SYS-B1-1 | EXHAUST FAN SYSTEM | HVAC Specific Products and Equipment | None | true
HVAC SYS-1 | HVAC SYSTEM | HVAC Specific Products and Equipment | None | true
TEST SYS-1 | HVAC TESTING SYSTEM | HVAC Specific Products and Equipment | None | true
EAF SYS-B1-1 | LAB EXHAUST FAN SYSTEM | HVAC Specific Products and Equipment | None | true
AHU-R-1 | AIR HANDLER | HVAC Specific Products and Equipment | Vinyl Sticker | false
PAHU-1-1 | PACKAGED AIR HANDLER UNIT | HVAC Specific Products and Equipment | Vinyl Sticker | false
FLTB-1-1 | FILTER BANK | HVAC Specific Products and Equipment | Vinyl Sticker | false
FLTB-1-1 | ZONE DIFFUSER FILTER | HVAC Specific Products and Equipment | Vinyl Sticker | false
EAF-1 | EXHAUST FAN | HVAC Specific Products and Equipment | Vinyl Sticker | false
EAF-1-1 | LAB EXHAUST FAN | HVAC Specific Products and Equipment | Vinyl Sticker | false
RAF-R-1 | RETURN FAN | HVAC Specific Products and Equipment | None | false
SAF-B1-1 | SUPPLY FAN | HVAC Specific Products and Equipment | None | false
ACMPR-1-1 | AIR COMPRESSOR | HVAC Specific Products and Equipment | Vinyl Sticker | false
HMD-B1-1 | HUMIDIFIER | HVAC Specific Products and Equipment | Vinyl Sticker | false
CVE-B1-1 | CAV EXHAUST BOX | HVAC Specific Products and Equipment | Vinyl Sticker | false
CVR-B1-1 | CAV RETURN BOX | HVAC Specific Products and Equipment | Vinyl Sticker | false
CVS-B1-1 | CAV SUPPLY BOX | HVAC Specific Products and Equipment | Vinyl Sticker | false
VVE-B1-1 | VAV EXHAUST BOX | HVAC Specific Products and Equipment | Vinyl Sticker | false
VVR-B1-1 | VAV RETURN BOX | HVAC Specific Products and Equipment | Vinyl Sticker | false
VVS-B1-1 | VAV SUPPLY BOX | HVAC Specific Products and Equipment | Vinyl Sticker | false
FEV-B1-1 | LAB FUMEHOOD EXHAUST AIR VALVE | HVAC Specific Products and Equipment | None | false
GEV-B1-1 | LAB GENERAL EXHAUST AIR VALVE | HVAC Specific Products and Equipment | None | false
SAV-B1-1 | LAB SUPPLY AIR VALVE | HVAC Specific Products and Equipment | None | false
CD-R-1 | DUCT BRANCH CONTROL DAMPER | HVAC Specific Products and Equipment | None | false
EAD-R-1 | EXHAUST AIR DAMPER | HVAC Specific Products and Equipment | None | false
OAD-R-1 | OUTSIDE AIR DAMPER | HVAC Specific Products and Equipment | None | false
RAD-1 | RETURN AIR DAMPER | HVAC Specific Products and Equipment | None | false
TAD-1 | TRANSFER AIR DAMPER | HVAC Specific Products and Equipment | None | false
CNDR-1-1 | COLD ROOM CONDENSER | HVAC Specific Products and Equipment | Vinyl Sticker | false
CDU-R-1 | CONDENSING UNIT | HVAC Specific Products and Equipment | Vinyl Sticker | false
COND-1-1 | SPLIT SYSTEM CONDENSER | HVAC Specific Products and Equipment | Vinyl Sticker | false
EVAP FC-1 | COLD ROOM EVAPORATOR FAN COIL | HVAC Specific Products and Equipment | Vinyl Sticker | false
PAC-R-1 | PACKAGED AIR CONDITIONER | HVAC Specific Products and Equipment | Vinyl Sticker | false
COLDRM SYS-1-1 | COLD ROOM SYSTEM | HVAC Specific Products and Equipment | Vinyl Sticker | false
AC-1-1 | SPLIT SYSTEM REFRIGERATION | HVAC Specific Products and Equipment | None | false
TSTAT-B1-1 | THERMOSTAT | HVAC Specific Products and Equipment | Vinyl Sticker | false
BLR-B1-1 | BOILER | HVAC Specific Products and Equipment | Vinyl Sticker | false
CHLR-B1-1 | CHILLER | HVAC Specific Products and Equipment | Vinyl Sticker | false
CT-R-1 | COOLING TOWER | HVAC Specific Products and Equipment | None | false
CHWC-B1-1 | CHILLED WATER COIL | HVAC Specific Products and Equipment | None | false
HHWC-B1-1 | HEATING HOT WATER COIL | HVAC Specific Products and Equipment | None | false
HCOIL-1-1 | HYDRONIC COIL | HVAC Specific Products and Equipment | None | false
CHWV-1-1 | CHW CONTROL VALVE | HVAC Specific Products and Equipment | None | false
DHWV-1-1 | DHW CONTROL VALVE | HVAC Specific Products and Equipment | None | false
HHWV-1-1 | HHW CONTROL VALVE | HVAC Specific Products and Equipment | None | false
STMV-1-1 | STEAM CONTROL VALVE | HVAC Specific Products and Equipment | None | false
BCU-B1-1 | BLOWER COIL UNIT | HVAC Specific Products and Equipment | Vinyl Sticker | false
FCU-B1-1 | FAN COIL UNIT | HVAC Specific Products and Equipment | Vinyl Sticker | false
FFU-B1-1 | FAN FILTER UNIT | HVAC Specific Products and Equipment | Vinyl Sticker | false
JACE-AX Bldg Code-1 | NIAGARA JACE | HVAC Specific Products and Equipment | Vinyl Sticker | false
CHWM-B1-1 | CHW BTU Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
CO2M-B1-1 | CO2 Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
CO4M-B1-1 | CO4 Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
DHWM-B1-1 | DHW BTU Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
ELCM-B1-1 | Electric Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
HHWM-B1-1 | HHW BTU Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
NGM-B1-1 | Natural Gas Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
N2M-B1-1 | Nitrogen Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
WTRM-B1-1 | Water Meter | HVAC Specific Products and Equipment | Metal Dogtag | false
BAS-1 | BUILDING CONTROLS SYSTEM | Information and Communication Specific Products and Equipment | None | true
BI SYS-1 | BUILDING INTERIOR SYSTEM | Interior and Finish Products | None | true
CIEL SYS-1-1 | CEILING SYSTEM | Interior and Finish Products | None | true
FLR SYS-1-1 | FLOORING SYSTEM | Interior and Finish Products | None | true
DEW-1-1 | DEWAR | Medical and Laboratory Equipment | Vinyl Sticker | false
FH-B1-1 | FUME HOOD CABINET | Medical and Laboratory Equipment | Vinyl Sticker | false
FHC-B1-1 | FUME HOOD CANOPY | Medical and Laboratory Equipment | None | false
DR SYS-1-1 | INTERIOR DOOR SYSTEM | Openings, Passages, and Protection Products | None | true
MNT DR-1-1 | MAINTENANCE DOOR SYSTEM | Openings, Passages, and Protection Products | None | true
SPLT DR-1-1 | SPECIALTY DOORS | Openings, Passages, and Protection Products | None | false
WND SYS-1-1 | WINDOW SYSTEM | Openings, Passages, and Protection Products | None | true
CND RSYS-1-1 | CONDENSATE RECOVERY SYSTEM | Plumbing Specific Products and Equipment | Vinyl Sticker | false
DHW SYS-1-1 | DHW SYSTEM | Plumbing Specific Products and Equipment | None | false
EMG WSH-1-1 | EMERGENCY WASH | Plumbing Specific Products and Equipment | Vinyl Sticker | false
EWASH-1-1 | EMERGENCY WASH SYSTEM | Plumbing Specific Products and Equipment | None | true
HHW SYS-1-1 | HHW SYSTEM | Plumbing Specific Products and Equipment | None | false
WS-1-1 | HYDRATION STATION | Plumbing Specific Products and Equipment | Vinyl Sticker | false
INTC-1-1 | OIL INTERCEPTOR | Plumbing Specific Products and Equipment | None | false
PLB SYS-1-1 | PLUMBING SYSTEM | Plumbing Specific Products and Equipment | None | true
SFTR-1-1 | SOFTENER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
CHW HX-B1-1 | CHILLED WATER HEAT EXCHANGER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
DHW HX-1-1 | DOMESTIC HOT WATER HEAT EXCHANGER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
HHW HX-B1-1 | HEATING HOT WATER HEAT EXCHANGER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
PCHW HX-B1-1 | PROCESS CHILLED WATER HEAT EXCHANGER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
ASPR-1-1 | AIR SEPARATOR | Plumbing Specific Products and Equipment | None | false
APTK-1-1 | AIR PRESSURE TANK | Plumbing Specific Products and Equipment | Vinyl Sticker | false
ATK-1-1 | AIR TANK | Plumbing Specific Products and Equipment | Vinyl Sticker | false
BWTK-1-1 | BRINE WATER TANK | Plumbing Specific Products and Equipment | Vinyl Sticker | false
ET-1-1 | EXPANSION TANK | Plumbing Specific Products and Equipment | Vinyl Sticker | false
FTANK-1-1 | FUEL TANK | Plumbing Specific Products and Equipment | Vinyl Sticker | false
WTNK-1-1 | WATER TANK | Plumbing Specific Products and Equipment | Vinyl Sticker | false
CHWP-B1-1 | CHILLED WATER PUMP | Plumbing Specific Products and Equipment | Vinyl Sticker | false
CDWP-B1-1 | CONDENSER WATER PUMP | Plumbing Specific Products and Equipment | Vinyl Sticker | false
DHWP-B1-1 | DOMESTIC HOT WATER PUMP | Plumbing Specific Products and Equipment | Vinyl Sticker | false
HHWP-B1-1 | HEATING HOT WATER PUMP | Plumbing Specific Products and Equipment | Vinyl Sticker | false
ICWP-B1-1 | INDUSTRIAL COLD WATER PUMP | Plumbing Specific Products and Equipment | Vinyl Sticker | false
IHWP-B1-1 | INDUSTRIAL HOT WATER PUMP | Plumbing Specific Products and Equipment | Vinyl Sticker | false
EWH-1 | ELECTRIC WATER HEATER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
GWH-1-1 | GAS WATER HEATER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
STMH-1-1 | STEAM WATER HEATER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
BFP-1-1 | BACKFLOW PREVENTER | Plumbing Specific Products and Equipment | Metal Dogtag | false
FLT-R-1 | WATER FILTER | Plumbing Specific Products and Equipment | Vinyl Sticker | false
GRNDS-1-1 | GROUNDS EQUIPMENT | Site Products | None | false
GRNDS SYS-1 | GROUNDS SYSTEM | Site Products | None | true
IRR SYS-1-1 | IRRIGATION SYSTEM | Site Products | None | true
OUT-1-1 | OUTDOOR SPACE | Site Products | None | false
PRKG SYS-1-1 | PARKING AND PATHWAYS SYSTEM | Site Products | None | true
PAYS-1-1 | PAY STATION | Site Products | Vinyl Sticker | false
BLDG-1-1 | BUILDING | Specialty Products | None | false
COMNX-1-1 | COMMON AREA SYSTEM | Specialty Products | None | true
REST SYS-1-1 | RESTROOM SYSTEM | Specialty Products | None | true
BE SYS-1 | BUILDING EXTERIOR SYSTEM | Structural and Interior Enclosure Products | None | true
ROOF SYS-1-1 | ROOFING AND COMPONENTS SYSTEM | Structural and Interior Enclosure Products | None | true
BUTL SYS-1 | BUILDING UTILITY SYSTEM | Utility and Transportation Products | None | true
CHEMX-1-1 | CHEMICAL CONTROLLER | Utility and Transportation Products | Vinyl Sticker | false
CHW SYS-B1-1 | CHILLED WATER SYSTEM | Utility and Transportation Products | None | false
STMGEN-B1-1 | CLEAN STEAM GENERATOR | Utility and Transportation Products | Vinyl Sticker | false
COGEN-1-1 | CO-GEN SYSTEM | Utility and Transportation Products | None | false
CMPR ASYS-1-1 | COMPRESSED AIR SYSTEM | Utility and Transportation Products | None | false
CND RCR-1-1 | CONDENSATE RECEIVER | Utility and Transportation Products | Vinyl Sticker | false
CDW SYS-1-1 | CONDENSER WATER SYSTEM | Utility and Transportation Products | None | false
EMSS SYS-1-1 | CONTINUOUS EMISSIONS MONITORING SYSTEM | Utility and Transportation Products | None | false
DAR-1-1 | DEAERATOR | Utility and Transportation Products | Metal Dogtag | false
DIWU-1-1 | DEIONIZED WATER UNIT | Utility and Transportation Products | Metal Dogtag | false
POT-B1-1 | POT FEEDER | Utility and Transportation Products | Metal Dogtag | false
PGEN SYS-1-1 | POWER GENERATION SYSTEM | Utility and Transportation Products | None | false
RDGR-1-1 | REDUCTION GEAR | Utility and Transportation Products | Metal Dogtag | false
ROU-1-1 | REVERSE OSMOSIS UNIT | Utility and Transportation Products | Metal Dogtag | false
STM SYS-1-1 | STEAM SYSTEM | Utility and Transportation Products | None | false
UTIL SYS-1-1 | UTILITY PLANT COMPONENT EQUIPMENT | Utility and Transportation Products | None | false
VAC-1 | VACUUM PUMP | Utility and Transportation Products | Vinyl Sticker | false
CAR-1-1 | VEHICLE | Utility and Transportation Products | Metal Dogtag | false
WCHM SYS-1-1 | WATER CHEMISTRY SYSTEM | Utility and Transportation Products | None | false
WTRT SYS-1-1 | WATER TREATMENT SYSTEM | Utility and Transportation Products | None | false

## BAS Point Name Intro
Updated:
2018-08-22
A. Caltech BMS Naming Convention & Smart Commissioning-Ready Requirements
1. General Point Naming Methodology
a. Naming Convention Scope & Purpose - The “Caltech HVAC Equip and Control Point Naming Standards” document provides naming conventions for HVAC controls points belonging to standard controls programs (e.g. VAV Zone, Fume hood Lab Zone, AHU, etc.) as well as conventions for HVAC equipment schedule names. This HVAC Equip and Control Point Naming Standards shall ONLY be used for points that are monitored, overridden or otherwise accessed by the BMS operator during operations and/or the commissioning authority (CxA) during commissioning. Other points that can be accessed through the BMS network that are native to devices such as VFDs, BTU meters, etc. that are not accessed by operations staff, Cx, GUI or explicitly used for controls or operations are not required to follow a standard naming convention in haystack. This Caltech BMS Naming Convention seeks to be as comprehensive as practical, however it does not encapsulate all potential points for every building controls system. The controls contractor shall use the Caltech HVAC Equip and Control Point Naming Standards. When additional controls points are necessary, the controls contractor shall follow the guiding principles of the Caltech HVAC Equip and Control Point Naming Standards to complete the naming of the remaining points. Any new names generated during a project shall be shared with Caltech prior to programming for review.
c. Naming Convention Update Cycles - This Caltech BMS Naming Convention has been created based on a review of the existing name abbreviations used across Caltech Niagara AX stations. With each new controls project, the Caltech BMS Naming Convention should be updated so that it remains relevant and comprehensive.
2. Specific Point Naming Convention Rules
a. Creating New Point Names - If a required controls point is not explicitly defined in the Caltech HVAC Equip and Control Point Naming Standards the contractor should rely on the same abbreviations and syntax of the standard to create additional points. The order of abbreviations does matter. All the naming conventions are constructed for easy sorting by sub-program. For example, all return fan related points on the AHU start with "RetFan". Any newly created point names shall be reviewed as part of the point review process.
b. Specifying Names for Duplicate Points - If there are multiple identical sub-programs or controllers that live on the same single program (e.g. fume hood lab with multiple air valves), append the end of the point name with "_1, _2, etc.". For example, a zone program with two supply valves will have two supply damper command points that should be written as: "SupDmprCmd_1, SupDmprCmd_2" .
This methodology allows the naming to easily accommodate controllers that have multiple supply/exhaust valves, occupancy sensors, thermostats, fans, dampers, etc. without having to explicitly define each of these points in the Caltech HVAC Equip and Control Point Naming Standards libraries.
c. Point Name Character Length - All point names in the Caltech BMS Naming Convention shall be 18 characters or less in order to be compatible with the limitations of Niagara AX display names. Where necessary, a clarification is provided to describe the full name of the point.
3. Commissioning Requirements
a. Haystack Compatability - All commissioned projects require a controls system that is haystack compatible. On Niagara AX platforms, a haystack service jar file shall be installed on each supervisory JACE that belongs to the project.
b. Point Organization and Naming - All points that are used for monitoring or override during the commissioning process shall be organized into a logical and simple folder structure under each controller. The controllers shall be named to match the equipment it serves, as defined in this design documentation. All points within these folders shall follow the standard point naming convention.
c. Commissioning Overrides - All projects require a subset of points that have override capability for commissioning functional testing purposes. The controls contractor shall review the pertinent design guidelines and naming convention for specific commissioning override point expectations. The CxA shall provide to the contractor the definitive list of required commissioning override (CxOvrd) points prior to the approval of a building automation systems submittal.
d. O&M Overrides - All commissioned projects require a subset of points that have override capability for the purposes of operations & maintenance. These points shall be able to be overridden through the BMS graphics pages. The contractor shall review the pertinent design guidelines and naming convention for specific operator override point expectations. The contractor shall include in their graphics submittal what BMS operator override (OpsOvrd) points shall be available to be reviewed by the CxA and Caltech O&M staff.
e. Commissioning Override Naming - In the case where there are required CxOvrd points that are not also OpsOvrd points, separate points shall be created for these purposes and shall be explicitly defined by appending the end of the standard point with “_Ovrd”. Points that fall under this category are often sensor points (e.g. zone temp sensor override point would be called ZnTmp_Ovrd) that would typically not be written to be overrideable. These points shall have the standard write-level array and override duration features of a native writable AX point.
f. Point Naming & Override Review - All commissioned projects require a point naming and point override review as part of the commissioning process BEFORE proceeding with the full deployment of the programming across a project. This avoids unnecessary duplication and cleanup of naming and override point issues. It is the responsibility of the contractor to inform the CxA when a program is ready for point review.
g. Controls Bench Testing - Projects shall include bench testing of the controls programming and database prior to deployment in the field. Bench testing shall include review of the programming logic for typical systems (within native environment preferred), review of point naming for compliance with Caltech standards, testing remote connectivity to Caltech SkySpark (or surrogate) server, review of point override capability (both for Cx through Haystack and through BMS for Ops), and review of typical GUI pages.
Each standard naming library tab in this workbook represents a typical controls program type.
| Tab/Sheet Name | Description
1 | TU-SAV Zone | Controls points list for a typical Supply Air Valve with reheat program that includes zone/thermostat controls. Includes naming for supply valves, reheat valves, zone comfort, and occupancy controls points.
2 | TU-EAV | Controls points list for a typical exhaust air valve program. Exhaust air valve can be general exhaust or serve a fumehood. Fumehood controller specific points under 3-TU-Fumehood
3 | TU-Fumehood | Controls points list for a typical Fumehood controller. Refer to TU-EAV for any exhaust air valve specific points.
4 | AHU SingleDuct | Controls points list for a typical Single Duct VAV with reheat zone program. Includes naming for supply valves, reheat valves, zone comfort, and occupancy controls points.
5 | AHU DualDuct | Controls points list for a typical Dual Duct VAV with reheat zone program. Includes naming for supply valves, reheat valves, zone comfort, and occupancy controls points.
6 | BldgWaterLoops | Controls points list for a typical building-level hydronic loop. Includes heat exchanger points, pump points, btu meter points, temp and pressure monitoring, pressure control valve points
Naming Standards Table Column Definitions
| Naming Table Column Name | Column Description
| StandardName | The name to be used as the display name in the building automations controls syste (BMS).
| Example_Value | An example of a current value for this point.
| TrendLocally | Indicates whether this point should be trended within the local supervisor
| OverrideAbility | Indicates whether this point shall be capable of being overridden within the BMS. Two levels of override ability are designated (see the 'Spec' sheet for further detail on how these are defined). (1) Commissioning overrides (CxOvrd); (2) Operator overrides (OpOvrd)
| IncldOnGraphic | Indicates whether this point shall be included in the BMS graphics.
| Full Name | Full description of the control point.
| Additional Description | Indicates any additional description or explanation of purpose/usage

## VVS Zone
Length of Name | Standard Name | Example Value | Trend Locally | Override Ability | Incld On Graphic | Full Name | Additional Description
10 | AirChanges | 5 |  |  |  | Space Air Changes | For pressurized zones (e.g. labs)
7 | AirFlow | 0 cfm | YES | CxOvrd | YES | Air Flow
9 | AirFlowDp | -0.0 in/wc | YES | CxOvrd | YES | Air Flow Differential Pressure
12 | AirFlowMaxSp | 580 cfm |  |  |  | Air Flow Effective Max Setpoint
12 | AirFlowMinSp | 0 cfm |  |  |  | Air Flow Effective Min Setpoint
9 | AirFlowSp | 0 cfm | YES | CxOvrd | YES | Air Flow Effective Setpoint
19 | AirFlowOccMaxCoolSp | 580 cfm |  |  |  | AirFlow Max Occupied Cooling Setpoint (design setpoint)
19 | AirFlowOccMaxHeatSp | 290 cfm |  |  |  | AirFlow Max Occupied Heat Setpoint (design setpoint)
15 | AirFlowOccMinSp | 174 cfm |  |  |  | AirFlow Min Occupied Setpoint (design setpoint)
16 | AirFlowStandbySp | 174 cfm |  |  |  | AirFlow Standby Setpoint (design setpoint)
14 | AirFlowUnoccSp | 174 cfm |  |  |  | AirFlow Unoccupied Setpoint (design setpoint)
16 | CoolDemandLimit1 | 1 |  |  |  | Cooling Demand Limit Level 1 | for zone-based demand reponse programs
16 | CoolDemandLimit2 | 2 |  |  |  | Cooling Demand Limit Level 2 | for zone-based demand reponse programs
16 | CoolDemandLimit3 | 4 |  |  |  | Cooling Demand Limit Level 3 | for zone-based demand reponse programs
13 | SACoolRequest | 0 |  |  |  | Cooling Request (to AHU) | For demand based trim & respond setpoint reset programs (per ASHRAE)
18 | SACoolRequestDelay | 2.0 min |  |  |  | Cooling Request - Time Delay | For demand based trim & respond setpoint reset programs (per ASHRAE)
9 | DamperCmd | 0 | YES | CxOvrd | YES | Damper Position Command
9 | DamperPos | 0 |  |  |  | Damper Position Feedback
6 | DATemp | 70.7 °F | YES | CxOvrd | YES | Discharge Air Temp
11 | DATempLpOut |  |  |  |  | Discharge Air Temp PID Loop Output
11 | DATempMaxSp | 95.0 °F |  |  |  | Discharge Air Temp Max Setpoint
11 | DATempMidSp | 95.0 °F |  |  |  | Discharge Air Temp Mid Setpoint | If a midway supply temp reset exists, prior to increasing supply air flow.
11 | DATempMinSp | 95.0 °F |  |  |  | Discharge Air Temp Min Setpoint
8 | DATempSp | 55.0 °F | YES | CxOvrd | YES | Discharge Air Temp Effective Setpoint
10 | DuctInTemp | 55.0 °F | YES | CxOvrd | YES | AHU Supply Air Temp | For points over network coming from serving AHU
8 | FlowBias | -77 cfm |  |  |  | Space Air Flow Bias | For pressurized zones (e.g. labs). Flow bias is the difference between exhaust and supply flows
10 | FlowBiasSp | -100 cfm |  |  |  | Space Air Flow Bias Setpoint | For pressurized zones (e.g. labs). Flow bias is the difference between exhaust and supply flows
13 | SAHeatRequest | 0 |  |  |  | Supply Air Temp Heating Request (to AHU) | For demand based trim & respond setpoint reset programs (per ASHRAE)
18 | SAHeatRequestDelay | 2.0 min |  |  |  | Supply Air Temp Heating Request Delay Time | For demand based trim & respond setpoint reset programs (per ASHRAE)
8 | HvacMode | Heat |  |  |  | Heating/Cooling/Deadband Mode
13 | HwHeatRequest |  |  |  |  | Heating Hot Water Temp Request (to bldg boiler/HX)
11 | HwDpRequest |  |  |  |  | Heating Hot Water Diff Pressure Request (to bldg HHW pump)
7 | HWValve | 0 |  |  |  | Supply Reheat Valve Position Feedback
10 | HWValveCmd | 0 | YES | CxOvrd | YES | Supply Reheat Valve Position Command
9 | OccSensor | TRUE |  |  |  | Occupany Motion Detection Sensor
10 | OccSensor1 | FALSE |  |  |  | Occupancy Sensor 1 Status | if multiple occupancy sensors in single zone
10 | OccSensor2 | FALSE |  |  |  | Occupancy Sensor 2 Status | if multiple occupancy sensors in single zone
9 | OccStatus | Unoccupied | YES | CxOvrd | YES | Occupancy Status | effective status, can be based on final combination of schedule and occupany detection sensors
8 | SpaceCO2 | 0 ppm | YES | CxOvrd | YES | Space CO2 Level (ppm)
13 | SpaceCO2MaxSp | 1000.0 ppm |  |  |  | Space CO2 Max Setpoint
13 | SpaceCO2MinSp | 800.0 ppm |  |  |  | Space CO2 Min Setpoint
7 | SpaceDp | -0.0 in/wc | YES | CxOvrd | YES | Space Differential Pressure
9 | SpaceDpSp | -0.0 in/wc | YES | CxOvrd | YES | Space Differential Pressure Setpoint | For pressurized zones (e.g. labs)
11 | SpaceCoolSp | 82.4 °F | YES | CxOvrd | YES | Space Temp Effective Cooling Setpoint
11 | SpaceHeatSp | 60.8 °F | YES | CxOvrd | YES | Space Temp Effective Heating Setpoint
11 | SpaceTempSp | 60.8 °F | YES | CxOvrd, OpsOvrd | YES | Space Temp Effective Setpoint | if heating/cooling mode rolls up into a single effective setpoint, otherwise use individual htg/clg setpoints
9 | SpaceTemp | 75.6 °F | YES | CxOvrd | YES | Space Temp
12 | SpaceTempErr | 1.2 °F |  |  |  | Space Temp Error From Effective Setpoint
15 | SAStaticRequest | 0 |  |  |  | Supply Air Static Pressure Request | For demand based trim & respond setpoint reset programs (per ASHRAE)
20 | SAStaticRequestDelay | 2.0 min |  |  |  | Supply Air Static Pressure Request Delay | For demand based trim & respond setpoint reset programs (per ASHRAE)
15 | TempCoolSpHiLim | 85.0 °F |  | CxOvrd |  | Zone Temp Cooling Setpoint High Limit
15 | TempCoolSpLoLim | 72.0 °F |  | CxOvrd |  | Zone Temp Cooling Setpoint Low Limit
15 | TempHeatSpHiLim | 72.0 °F |  | CxOvrd |  | Zone Temp Heating Setpoint High Limit
15 | TempHeatSpLoLim | 65.0 °F |  | CxOvrd |  | Zone Temp Heating Setpoint Low Limit
11 | TempLocalSp | 72.0 °F |  |  |  | Zone Temp Local User Setpoint
17 | TempLocalSpEnable | Yes |  |  |  | Zone Temp Local User Setpoint Control Enable | To allow occupants to set thermostat setpoint locally
13 | TempMaxOffset | 4.0 °F |  | CxOvrd |  | Zone Max Temp Offset (for alarming)
13 | TempMinOffset | -4.0 °F |  | CxOvrd |  | Zone Min Temp Offset (for alarming)
13 | TempOccCoolSp | 73.0 °F |  | CxOvrd |  | Zone Temp Occupied Cooling Setpoint
13 | TempOccHeatSp | 70.0 °F |  | CxOvrd |  | Zone Temp Occupied Heating Setpoint
17 | TempStandbyCoolSp | 80.0 °F |  | CxOvrd |  | Zone Temp Standby Cooling Setpoint
17 | TempStandbyHeatSp | 60.0 °F |  | CxOvrd |  | Zone Temp Standby Heat Setpoint
15 | TempUnoccCoolSp | 85.0 °F |  | CxOvrd |  | Zone Temp Unoccupied Cooling Setpoint
15 | TempUnoccHeatSp | 55.0 °F |  | CxOvrd |  | Zone Temp Unoccupied Heating Setpoint
12 | TempDmdLpOut | 0% |  |  |  | Zone Heating/Cooling Load Demand Loop Output Signal | If a single PID loop exists for both heating and cooling (e.g. -100% to 100%)
16 | TempCoolDmdLpOut | 0% |  |  |  | Zone Cooling Load Demand Loop Output Signal
16 | TempHeatDmdLpOut | 0% |  |  |  | Zone Heating Load Demand Loop Output Signal
12 | WindowSwitch | Closed |  |  |  | Window Open/Close Status

## VVE
Length of Name | Standard Name | Example Value | Trend Locally | Override Ability | Incld On Graphic | Full Name | Additional Description
7 | AirFlow | 323 cfm | YES | CxOvrd | YES | EV-1 Exhaust Flow
12 | AirFlowMaxSp | 750 cfm |  |  |  | EV-1 Exhaust Flow Maximum Setpoint
12 | AirFlowMinSp | 0 cfm |  |  |  | EV-1 Exhaust Flow Minimum Setpoint
9 | AirFlowSp | 120 cfm | YES | OpsOvrd, CxOvrd | YES | EV-1 Exhaust Flow Effective Setpoint
9 | DamperCmd | 20.0 % | YES | OpsOvrd, CxOvrd | YES | EV-1 Exhaust Damper Position Command
9 | DamperPos | 20.0 % | YES |  | YES | EV-1 Exhaust Damper Position Feedback
15 | LowAirFlowAlarm | Normal |  |  |  | EV-1 Exhaust Flow Low Alarm
6 | EATemp |  | YES |  | YES | Exhaust Air Temperature Sensor
11 | EAFlowLpOut |  |  |  |  | Exhaust Air Flow Setpoint Control PID Loop Out

## Lab Zone, multi equips
Length of Name | Standard Name | Example Value | Trend Locally | Override Ability | Incld On Graphic | Full Name | Additional Description
10 | AirChanges | 5 |  |  |  | Space Air Changes | For pressurized zones (e.g. labs)
10 | DuctInTemp | 55.0 °F | YES | CxOvrd | YES | AHU Supply Air Temp | For points over network coming from serving AHU
10 | SV1AirFlow | 0 cfm | YES | CxOvrd | YES | SV-1 Air Flow | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
12 | SV1AirFlowDp | -0.0 in/wc | YES | CxOvrd | YES | SV-1 Air Flow Differential Pressure | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
15 | SV1AirFlowMaxSp | 580 cfm |  |  |  | SV-1 Air Flow Effective Max Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
15 | SV1AirFlowMinSp | 0 cfm |  |  |  | SV-1 Air Flow Effective Min Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
22 | SV1AirFlowOccMaxCoolSp | 580 cfm |  |  |  | SV-1 Air Flow Max Occupied Cooling Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
22 | SV1AirFlowOccMaxHeatSp | 290 cfm |  |  |  | SV-1 Air Flow Max Occupied Heat Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
18 | SV1AirFlowOccMinSp | 174 cfm |  |  |  | SV-1 Air Flow Min Occupied Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
12 | SV1AirFlowSp | 0 cfm | YES | CxOvrd | YES | SV-1 Air Flow Effective Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
19 | SV1AirFlowStandbySp | 174 cfm |  |  |  | SV-1 Air Flow Standby Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
17 | SV1AirFlowUnoccSp | 174 cfm |  |  |  | SV-1 Air Flow Unoccupied Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
14 | SVTotalAirFlow | 0 cfm | YES | CxOvrd | YES | Supply Air Flow Total (from all air valves/VAV boxes)
12 | SV1DamperCmd | 0 | YES | CxOvrd | YES | SV-1 Damper Position Command | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
12 | SV1DamperPos | 0 |  |  |  | SV-1 Damper Position Feedback | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
9 | SV1DATemp | 70.7 °F | YES | CxOvrd | YES | SV-1 Discharge Air Temp | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
14 | SV1DATempLpOut |  |  |  |  | SV-1 Discharge Air Temp PID Loop Output | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
14 | SV1DATempMaxSp | 95.0 °F |  |  |  | SV-1 Discharge Air Temp Max Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
14 | SV1DATempMidSp | 95.0 °F |  |  |  | SV-1 Discharge Air Temp Mid Setpoint | If a midway supply temp reset exists, prior to increasing supply air flow.
14 | SV1DATempMinSp | 95.0 °F |  |  |  | SV-1 Discharge Air Temp Min Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
11 | SV1DATempSp | 55.0 °F | YES | CxOvrd | YES | SV-1 Discharge Air Temp Effective Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "SV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. SV1, SV2, etc.)
16 | SV1HwHeatRequest |  |  |  |  | Heating Hot Water Temp Request (to bldg boiler/HX)
10 | SV1HWValve | 0 |  |  |  | Supply Reheat Valve Position Feedback
13 | SV1HWValveCmd | 0 | YES | CxOvrd | YES | Supply Reheat Valve Position Command
16 | SV1SACoolRequest | 0 |  |  |  | Cooling Request (to AHU) | For demand based trim & respond setpoint reset programs (per ASHRAE)
21 | SV1SACoolRequestDelay | 2.0 min |  |  |  | Cooling Request - Time Delay | For demand based trim & respond setpoint reset programs (per ASHRAE)
16 | SV1SAHeatRequest | 0 |  |  |  | Supply Air Temp Heating Request (to AHU) | For demand based trim & respond setpoint reset programs (per ASHRAE)
21 | SV1SAHeatRequestDelay | 2.0 min |  |  |  | Supply Air Temp Heating Request Delay Time | For demand based trim & respond setpoint reset programs (per ASHRAE)
10 | EV1AirFlow | 0 cfm | YES | CxOvrd | YES | EV-1 Air Flow | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
12 | EV1AirFlowDp | -0.0 in/wc | YES | CxOvrd | YES | EV-1 Air Flow Differential Pressure | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
15 | EV1AirFlowMaxSp | 580 cfm |  |  |  | EV-1 Air Flow Effective Max Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
15 | EV1AirFlowMinSp | 0 cfm |  |  |  | EV-1 Air Flow Effective Min Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
22 | EV1AirFlowOccMaxCoolSp | 580 cfm |  |  |  | EV-1 Air Flow Max Occupied Cooling Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
22 | EV1AirFlowOccMaxHeatSp | 290 cfm |  |  |  | EV-1 Air Flow Max Occupied Heat Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
18 | EV1AirFlowOccMinSp | 174 cfm |  |  |  | EV-1 Air Flow Min Occupied Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
12 | EV1AirFlowSp | 0 cfm | YES | CxOvrd | YES | EV-1 Air Flow Effective Setpoint | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
19 | EV1AirFlowStandbySp | 174 cfm |  |  |  | EV-1 Air Flow Standby Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
17 | EV1AirFlowUnoccSp | 174 cfm |  |  |  | EV-1 Air Flow Unoccupied Setpoint (design setpoint) | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
16 | EVTotalAirFlowSp | 0 cfm | YES | CxOvrd | YES | Exhaust Air Flow Total Setpoint (for all air valves/VAV boxes)
17 | GEVTotalAirFlowSp | 0 cfm | YES | CxOvrd | YES | General Exhaust Air Flow Total Setpoint (for all general exhaust air valves/VAV boxes)
14 | EVTotalAirFlow | 0 cfm | YES | CxOvrd | YES | Exhaust Air Flow Total (from all air valves/VAV boxes)
15 | GEVTotalAirFlow | 0 cfm | YES | CxOvrd | YES | General Exhaust Air Flow Total (from all general exhaust air valves/VAV boxes)
15 | FEVTotalAirFlow | 0 cfm | YES | CxOvrd | YES | Fumehood Exhaust Air Flow Total (from all general exhaust air valves/VAV boxes)
12 | EV1DamperCmd | 0 | YES | CxOvrd | YES | EV-1 Damper Position Command | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
12 | EV1DamperPos | 0 |  |  |  | EV-1 Damper Position Feedback | Use this convention if there is more than one VAV box or air valve under the same controller. "EV1" is example refering to to the supply air valve by its simplifed schedule tag (e.g. EV1, SV2, etc.)
9 | EV1EATemp |  | YES |  | YES | EV-1 Exhaust Air Temperature Sensor
16 | CoolDemandLimit1 | 1 |  |  |  | Cooling Demand Limit Level 1 | for zone-based demand reponse programs
16 | CoolDemandLimit2 | 2 |  |  |  | Cooling Demand Limit Level 2 | for zone-based demand reponse programs
16 | CoolDemandLimit3 | 4 |  |  |  | Cooling Demand Limit Level 3 | for zone-based demand reponse programs
8 | FlowBias | -77 cfm |  |  |  | Space Air Flow Bias | For pressurized zones (e.g. labs). Flow bias is the difference between exhaust and supply flows
10 | FlowBiasSp | -100 cfm |  |  |  | Space Air Flow Bias Setpoint | For pressurized zones (e.g. labs). Flow bias is the difference between exhaust and supply flows
8 | HvacMode | Heat |  |  |  | Heating/Cooling/Deadband Mode
11 | HwDpRequest |  |  |  |  | Heating Hot Water Diff Pressure Request (to bldg HHW pump)
9 | OccSensor | TRUE |  |  |  | Occupany Motion Detection Sensor
10 | OccSensor1 | FALSE |  |  |  | Occupancy Sensor 1 Status | if multiple occupancy sensors in single zone
10 | OccSensor2 | FALSE |  |  |  | Occupancy Sensor 2 Status | if multiple occupancy sensors in single zone
9 | OccStatus | Unoccupied | YES | CxOvrd | YES | Occupancy Status | effective status, can be based on final combination of schedule and occupany detection sensors
15 | SAStaticRequest | 0 |  |  |  | Supply Air Static Pressure Request | For demand based trim & respond setpoint reset programs (per ASHRAE)
20 | SAStaticRequestDelay | 2.0 min |  |  |  | Supply Air Static Pressure Request Delay | For demand based trim & respond setpoint reset programs (per ASHRAE)
8 | SpaceCO2 | 0 ppm | YES | CxOvrd | YES | Space CO2 Level (ppm)
13 | SpaceCO2MaxSp | 1000.0 ppm |  |  |  | Space CO2 Max Setpoint
13 | SpaceCO2MinSp | 800.0 ppm |  |  |  | Space CO2 Min Setpoint
11 | SpaceCoolSp | 82.4 °F | YES | CxOvrd | YES | Space Temp Effective Cooling Setpoint
7 | SpaceDp | -0.0 in/wc | YES | CxOvrd | YES | Space Differential Pressure
9 | SpaceDpSp | -0.0 in/wc | YES | CxOvrd | YES | Space Differential Pressure Setpoint | For pressurized zones (e.g. labs)
11 | SpaceHeatSp | 60.8 °F | YES | CxOvrd | YES | Space Temp Effective Heating Setpoint
9 | SpaceTemp | 75.6 °F | YES | CxOvrd | YES | Space Temp
12 | SpaceTempErr | 1.2 °F |  |  |  | Space Temp Error From Effective Setpoint
11 | SpaceTempSp | 60.8 °F | YES | CxOvrd, OpsOvrd | YES | Space Temp Effective Setpoint | if heating/cooling mode rolls up into a single effective setpoint, otherwise use individual htg/clg setpoints
16 | TempCoolDmdLpOut | 0% |  |  |  | Zone Cooling Load Demand Loop Output Signal
15 | TempCoolSpHiLim | 85.0 °F |  | CxOvrd |  | Zone Temp Cooling Setpoint High Limit
15 | TempCoolSpLoLim | 72.0 °F |  | CxOvrd |  | Zone Temp Cooling Setpoint Low Limit
12 | TempDmdLpOut | 0% |  |  |  | Zone Heating/Cooling Load Demand Loop Output Signal | If a single PID loop exists for both heating and cooling (e.g. -100% to 100%)
16 | TempHeatDmdLpOut | 0% |  |  |  | Zone Heating Load Demand Loop Output Signal
15 | TempHeatSpHiLim | 72.0 °F |  | CxOvrd |  | Zone Temp Heating Setpoint High Limit
15 | TempHeatSpLoLim | 65.0 °F |  | CxOvrd |  | Zone Temp Heating Setpoint Low Limit
11 | TempLocalSp | 72.0 °F |  |  |  | Zone Temp Local User Setpoint
17 | TempLocalSpEnable | Yes |  |  |  | Zone Temp Local User Setpoint Control Enable | To allow occupants to set thermostat setpoint locally
13 | TempMaxOffset | 4.0 °F |  | CxOvrd |  | Zone Max Temp Offset (for alarming)
13 | TempMinOffset | -4.0 °F |  | CxOvrd |  | Zone Min Temp Offset (for alarming)
13 | TempOccCoolSp | 73.0 °F |  | CxOvrd |  | Zone Temp Occupied Cooling Setpoint
13 | TempOccHeatSp | 70.0 °F |  | CxOvrd |  | Zone Temp Occupied Heating Setpoint
17 | TempStandbyCoolSp | 80.0 °F |  | CxOvrd |  | Zone Temp Standby Cooling Setpoint
17 | TempStandbyHeatSp | 60.0 °F |  | CxOvrd |  | Zone Temp Standby Heat Setpoint
15 | TempUnoccCoolSp | 85.0 °F |  | CxOvrd |  | Zone Temp Unoccupied Cooling Setpoint
15 | TempUnoccHeatSp | 55.0 °F |  | CxOvrd |  | Zone Temp Unoccupied Heating Setpoint
12 | WindowSwitch | Closed |  |  |  | Window Open/Close Status

## Fumehood
Length of Name | Standard Name | Example Value | Trend Locally | Override Ability | Incld On Graphic | Full Name | Additional Description
13 | ExhaustVolume | 299 cfm | YES |  | YES | FH-1 Fumehood Exhaust Flow | Accuvalve controllers refer to point as "Volume" instead of flow, so using that term.
12 | FaceVelocity | 100 ft/min | YES |  | YES | FH-1 Fumehood Face Velocity
19 | FaceVelocityHiAlarm | Normal |  |  | YES | FH-1 Fumehood Hi Face Velocity Alarm
19 | FaceVelocityLoAlarm | Normal |  |  | YES | FH-1 Fumehood Low Face Velocity Alarm
12 | SashPosition | 0 | YES |  | YES | FH-1 Fumehood Sash Position Fdk
19 | SashPositionHiAlarm | Safe |  |  | YES | FH-1 Fumehood High Sash Alarm

## AHU - Single Duct
Length of Name | Standard Name | Example Value | Trend Locally | Override Ability | On Graphic | Full Name | Additional Description
10 | BldgStatic | 0.05 in/wc | Yes |  | Yes | Building Static Pressure Sensor Reading
12 | BldgStaticSp | 0.05 in/wc | Yes | OpsOvrd, CxOvrd | Yes | Building Static Pressure Setpoint
15 | BldgStaticLpOut | 83.9% |  |  |  | Building Static Pressure PID Control Loop Signal Output
11 | CHWValveCmd | 0 % | Yes | OpsOvrd, CxOvrd | Yes | Chilled Water Valve Command
8 | CHWValve | 0 % | Yes |  | Yes | Chilled Water Valve Command Status
11 | CHWValveFbk | 0 % |  |  |  | Chilled Water Valve Feedback
8 | CHWRTemp | 50.3 °F | Yes |  | Yes | Chilled Water Return (Coil Leaving ) Temp
8 | CHWSTemp | 50.3 °F | Yes |  | Yes | Chilled Water Supply (Coil Entering) Temp
13 | EconEnableCmd | On | Yes | OpsOvrd, CxOvrd | Yes | Economizer Enable Command
16 | EconEnableStatus | On |  |  | Yes | Economizer Enable Status
11 | EFEnableCmd | On | YES | OpsOvrd, CxOvrd | YES | Exhaust / Relief Fan Enable Command | Use this when there is only one exhaust fan associated with AHU.
7 | EFFault | Normal | YES |  | YES | Exhaust / Relief Fan VFD Fault Status | Use this when there is only one exhaust fan associated with AHU.
8 | EFStatus | Running | YES |  | YES | Exhaust / Relief Fan Status | Use this when there is only one exhaust fan associated with AHU.
12 | EF1EnableCmd | On | YES | OpsOvrd, CxOvrd | YES | EF-1 Exhaust / Relief Fan Enable Command | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
9 | EF1Status | Running | YES |  | YES | EF-1 Exhaust / Relief Fan Status | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
14 | EF1FaultStatus | Normal | YES |  | YES | Exhaust / Relief Fan VFD Fault Status | Use this when there is only one exhaust fan associated with AHU.
11 | EADamperCmd | 15 % | YES | OpsOvrd, CxOvrd | YES | Exhaust Damper Position Command
8 | EADamper | 15 % |  |  | YES | Exhaust Damper Position Feedback
15 | FireAlarmStatus | Normal |  |  | YES | Fire Alarm Status
7 | HWRTemp | 100.0 °F | YES |  | YES | Heating Hot Water Coil Supply (Entering)Temp
7 | HWSTemp | 140.0 °F | YES |  | YES | Heating Hot Water Coil Supply (Entering)Temp
10 | HWValveCmd | 0 % | YES | OpsOvrd, CxOvrd | YES | Hot Water Valve Command
7 | HWValve | 0 % | YES |  | YES | Hot Water Valve Command Status
10 | HWValveFbk | 0 % |  |  |  | Hot Water Valve Feedback
14 | MinOADamperCmd | Open | YES | CxOvrd | YES | Minimum Outside Air Damper Position Command
6 | MATemp | 70.0 °F | YES |  | YES | Mixed Air Temp
11 | OADamperCmd | 15 % | YES | OpsOvrd, CxOvrd | YES | Outside Air Damper Position Command
8 | OADamper | 15 % | YES |  | YES | Outside Air Damper Position Command Status
11 | OADamperFbk | 15 % |  |  |  | Outside Air Damper Position Feedback
10 | OADResetSp | 15 % | YES |  | YES | Outside Air Damper Reset Effective Setpoint | if damper position reset present
13 | OADResetInput | 70 % |  |  |  | Outside Air Damper Reset Input (i.e. MaxCO2 or SFSpeed) | if using a Standard Sp Reset based on input (i.e. MaxCO2 or SFSpeed)
13 | OADResetInMax | 100 % |  | CxOvrd |  | Outside Air Damper Reset Input Maximum Setpoint | if using a Standard Sp Reset based on input (i.e. MaxCO2 or SFSpeed)
13 | OADResetInMin | 30 % |  | CxOvrd |  | Outside Air Damper Reset Input Minimum Setpoint | if using a Standard Sp Reset based on input (i.e. MaxCO2 or SFSpeed)
13 | OADResetSpMax | 40 % |  | CxOvrd |  | Outside Air Damper Reset Setpoint Maximum | if using a Standard Sp Reset based on input (i.e. MaxCO2 or SFSpeed)
13 | OADResetSpMin | 10 % |  | CxOvrd |  | Outside Air Damper Reset Setpoint Minimum | if using a Standard Sp Reset based on input (i.e. MaxCO2 or SFSpeed)
6 | OAFlow | 750 cfm | YES |  | YES | Outside Air Flow
10 | OAHumidity | 23 %RH |  |  | YES | Outside Air Humidity
6 | OATemp | 70.5 °F |  |  | YES | Outside Air Temp
11 | RAFlowTotal | 4250 cfm | YES |  | YES | Return Air Flow Total
10 | RAHumidity | 0.449 |  |  |  | Return Air Humidity
11 | RADamperCmd | 100 % |  | OpsOvrd, CxOvrd |  | Return Damper 1 - Damper Position Command
8 | RADamper | 100 % |  |  |  | Return Damper 1 - Damper Position Feedback
6 | RATemp | 73.4 °F | YES |  |  | Return Duct Air Temp
6 | RAFlow | 4250 cfm | YES |  | YES | RF-1 Return Air Duct Flow
4 | RFDp | 1.05 in/wc |  |  |  | Return Fan Differential Pressure | Use this when there is only one return fan associated with AHU.
11 | RFEnableCmd | On | Yes | OpsOvrd, CxOvrd | Yes | Return Fan Enable Command | Use this when there is only one return fan associated with AHU.
7 | RFFault | Normal | Yes |  |  | Return Fan VFD Fault | Use this when there is only one return fan associated with AHU.
7 | RFSpeed | 60 % | Yes | OpsOvrd, CxOvrd | Yes | Return Fan Speed Command | Use this when there is only one return fan associated with AHU.
8 | RFStatus | Running | Yes |  | Yes | Return Fan Status | Use this when there is only one return fan associated with AHU.
5 | RF1Dp | 1.05 in/wc |  |  |  | RF-1 Return Fan Differential Pressure | Use this convention if there is more than one return fan. "RF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. RF1, RF2, etc.)
12 | RF1EnableCmd | On | Yes | OpsOvrd, CxOvrd | Yes | RF-1 Return Fan Enable Command | Use this convention if there is more than one return fan. "RF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. RF1, RF2, etc.)
8 | RF1Fault | Normal | Yes |  |  | RF-1 Return Fan VFD Fault | Use this convention if there is more than one return fan. "RF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. RF1, RF2, etc.)
8 | RF1Speed | 60 % | Yes | OpsOvrd, CxOvrd | Yes | RF-1 Return Fan Speed Command | Use this convention if there is more than one return fan. "RF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. RF1, RF2, etc.)
9 | RF1Status | Running | Yes |  | Yes | RF-1 Return Fan Status | Use this convention if there is more than one return fan. "RF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. RF1, RF2, etc.)
4 | SFDp | 1.25 in/wc |  |  |  | Supply Fan Supply Air Differential Pressure | Use this when there is only one supply fan associated with AHU.
6 | SFFlow | 5000 cfm | Yes |  |  | Supply Fan Air Flow | Use this when there is only one supply fan associated with AHU.
11 | SFEnableCmd | On | Yes | OpsOvrd, CxOvrd | Yes | Supply Fan Enable Command | Use this when there is only one supply fan associated with AHU.
7 | SFSpeed | 70 % | Yes | OpsOvrd, CxOvrd | Yes | Supply Fan Speed Command | Use this when there is only one supply fan associated with AHU.
8 | SFStatus | Running | Yes |  | Yes | Supply Fan Status | Use this when there is only one supply fan associated with AHU.
7 | SFFault | Normal | Yes |  |  | Supply Fan VFD Fault Status | Use this when there is only one supply fan associated with AHU.
5 | SF1Dp | 1.25 in/wc |  |  |  | SF-1 Supply Air Differential Pressure | Use this convention if there is more than one supply fan. "SF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. SF1, SF2, etc.)
7 | SF1Flow | 5000 cfm |  |  | YES | SF-1 Supply Air Flow | Use this convention if there is more than one supply fan. "SF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. SF1, SF2, etc.)
12 | SF1EnableCmd | On | Yes | OpsOvrd, CxOvrd | Yes | SF-1 Supply Fan Enable Command | Use this convention if there is more than one supply fan. "SF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. SF1, SF2, etc.)
8 | SF1Speed | 70 % | Yes | OpsOvrd, CxOvrd | Yes | SF-1 Supply Fan Speed Command | Use this convention if there is more than one supply fan. "SF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. SF1, SF2, etc.)
9 | SF1Status | Running | Yes |  | Yes | SF-1 Supply Fan Status | Use this convention if there is more than one supply fan. "SF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. SF1, SF2, etc.)
8 | SF1Fault | Normal | Yes |  |  | SF-1 VFD Fault Status | Use this convention if there is more than one supply fan. "SF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. SF1, SF2, etc.)
11 | SpaceMaxCO2 | 0 |  |  |  | Space Max CO2 Setpoint | Used for or Outside Air Demand Reset
11 | SAFlowTotal | 5000 cfm | YES |  | YES | Supply Air Flow Total | If supply air flow from multiple fans needs to be totalized
8 | SAStatic | 2.00 in/wc | Yes |  | Yes | Supply Air Duct Static Pressure Sensor
10 | SAStaticSp | 2.00 in/wc | Yes | OpsOvrd, CxOvrd | Yes | Supply Air Duct Static Pressure Effective Setpoint
21 | SAStaticTNRIgnoredReq | 2 |  | CxOvrd |  | Supply Air Static Trim and Respond - Ignored Request | if using a demand-based trim & respond setpoint reset (per AHSRAE)
17 | SAStaticTNRSpInit | 0.50 in/wc |  | CxOvrd |  | Supply Air Static Trim and Respond - Initial Setpoint | if using a demand-based trim & respond setpoint reset (per AHSRAE)
16 | SAStaticTNRSpMax | 2.00 in/wc |  | CxOvrd |  | Supply Air Static Trim and Respond - Maximum Setpoint | if using a demand-based trim & respond setpoint reset (per AHSRAE)
16 | SAStaticTNRSpMin | 0.01 in/wc |  | CxOvrd |  | Supply Air Static Trim and Respond - Minimum Setpoint | if using a demand-based trim & respond setpoint reset (per AHSRAE)
14 | SAStaticTNRReq | 18 |  | CxOvrd |  | Supply Air Static Trim and Respond - Requests | if using a demand-based trim & respond setpoint reset (per AHSRAE)
20 | SAStaticTNRInitDelay | 600 seconds |  | CxOvrd |  | Supply Air Static Trim and Respond - Reset Initial Delay | if using a demand-based trim & respond setpoint reset (per AHSRAE)
18 | SAStaticTNRRespond | 0.02 in/wc |  | CxOvrd |  | Supply Air Static Trim and Respond - Respond | if using a demand-based trim & respond setpoint reset (per AHSRAE)
21 | SAStaticTNRRespondMax | 0.50 in/wc |  | CxOvrd |  | Supply Air Static Trim and Respond - Respond Max | if using a demand-based trim & respond setpoint reset (per AHSRAE)
19 | SAStaticTNRTimeStep | 120 seconds |  | CxOvrd |  | Supply Air Static Trim and Respond - TimeStep | if using a demand-based trim & respond setpoint reset (per AHSRAE)
15 | SAStaticTNRTrim | -0.02 in/wc |  | CxOvrd |  | Supply Air Static Trim and Respond - Trim | if using a demand-based trim & respond setpoint reset (per AHSRAE)
6 | SATemp | 52.3 °F | Yes |  | Yes | Supply Air Temperature Sensor
8 | SATempSp | 52.2 °F | Yes |  | Yes | Supply Air Temperature Effective Setpoint
11 | SATempLpOut | 83.9% |  |  |  | Supply Temp Control Loop - Output Signal
13 | SATResetInput | 70.5 °F |  | CxOvrd |  | Supply Air Temperature Reset Input (i.e. OATemp) | if using a OATemp based Sp Reset
13 | SATResetInMax | 70.0 °F |  | CxOvrd |  | Supply Air Temperature Reset Input Maximum Setpoint | if using a OATemp based Sp Reset
13 | SATResetInMin | 60.0 °F |  | CxOvrd |  | Supply Air Temperature Reset Input Minimum Setpoint | if using a OATemp based Sp Reset
13 | SATResetSpMax | 60.0 °F |  | CxOvrd |  | Supply Air Temperature Reset Setpoint Maximum | if using a OATemp based Sp Reset
13 | SATResetSpMin | 55.5 °F |  | CxOvrd |  | Supply Air Temperature Reset Setpoint Minimum | if using a OATemp based Sp Reset
19 | SATempTNRIgnoredReq | 2 |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Ignored Request | if using a demand-based trim & respond setpoint reset (per AHSRAE)
15 | SATempTNRSpInit | 52.2 °F |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Initial Setpoint | if using a demand-based trim & respond setpoint reset (per AHSRAE)
14 | SATempTNRSpMax | 60.0 °F |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Maximum Setpoint | if using a demand-based trim & respond setpoint reset (per AHSRAE)
14 | SATempTNRSpMin | 60.0 °F |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Minimum Setpoint | if using a demand-based trim & respond setpoint reset (per AHSRAE)
12 | SATempTNRReq | 18 |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Requests | if using a demand-based trim & respond setpoint reset (per AHSRAE)
18 | SATempTNRInitDelay | 600 seconds |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Reset Initial Delay | if using a demand-based trim & respond setpoint reset (per AHSRAE)
16 | SATempTNRRespond | -0.05 °F |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Respond | if using a demand-based trim & respond setpoint reset (per AHSRAE)
19 | SATempTNRRespondMax | -2.0 °F |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Respond Max | if using a demand-based trim & respond setpoint reset (per AHSRAE)
17 | SATempTNRTimeStep | 120 seconds |  | CxOvrd |  | Supply Air Temperature Trim and Respond - TimeStep | if using a demand-based trim & respond setpoint reset (per AHSRAE)
13 | SATempTNRTrim | 0.1 °F |  | CxOvrd |  | Supply Air Temperature Trim and Respond - Trim | if using a demand-based trim & respond setpoint reset (per AHSRAE)
8 | RAStatic | 1.367 in/wc | Yes |  | Yes | Return Air Static Pressure Sensor
10 | RAStaticSp | 1.250 in/wc | Yes | OpsOvrd, CxOvrd | Yes | Return Air Static Pressure Effective Setpoint
13 | RAStaticLpOut | 0% |  |  |  | Return Air Static Pressure Control Loop Output
13 | RAStaticMaxSp | 0.450 in/wc |  | CxOvrd |  | Return Air Static Pressure Max Setpoint
13 | RAStaticMinSp | 0.000 in/wc |  | CxOvrd |  | Return Air Static Pressure Min Setpoint

## Exhaust System
Length of Name | Standard Name | Example Value | Trend Locally | Override Ability | Incld On Graphic | Full Name | Additional Description
12 | BypassDamper | 15% | YES |  | YES | Outside Air Bypass Damper Position Feedback
15 | BypassDamperCmd | 15% | YES |  | YES | Outside Air Bypass Damper Position Cmd
4 | EADp | 0.05 in/wc | YES | CxOvrd | YES | Exhaust Air Differential Pressure
6 | EAFlow | 50cfm | YES | CxOvrd | YES | Exhaust Air Flow
8 | EAFlowSp | 50cfm | YES | CxOvrd | YES | Exhaust Air Flow Effective Setpoint
11 | EAFlowMaxSp | 50cfm | YES | CxOvrd | YES | Exhaust Air Flow Max Setpoint | if an exhaust air flow setpoint reset is being used
11 | EAFlowMinSp | 50cfm | YES | CxOvrd | YES | Exhaust Air Flow Min Setpoint | if an exhaust air flow setpoint reset is being used
11 | EAFlowLpOut |  |  |  |  | Exhaust Air Flow Setpoint Control PID Loop Output
8 | EAStatic | -0.5 in/wc | YES | CxOvrd | YES | Exhaust Air Static Pressure
13 | EAStaticMaxSp | -2.0 in/wc |  |  | YES | Exhaust Air Static Pressure Max Setpoint | if an exhaust air static pressures setpoint reset is being used
13 | EAStaticMinSp | -0.5 in/wc |  |  | YES | Exhaust Air Static Pressure Min Setpoint | if an exhaust air static pressures setpoint reset is being used
11 | EAStaticReq | 3 |  |  | YES | Exhaust Air Static Pressure Setpoint Reset Requests (from zones) | if a trim & respond exhaust air static pressures setpoint reset is being used (per ASHRAE)
10 | EAStaticSp | -0.5 in/wc | YES | CxOvrd | YES | Exhaust Air Static Pressure Effective Setpoint
13 | EAStaticLpOut |  | YES |  |  | Exhaust Air Static Pressure Setpoint Control PID Loop Output
11 | EFEnableCmd | On | YES | CxOvrd,OpsOvrd | YES | Exhaust Fan Enable Cmd | Use this when there is only one exhaust fan associated with AHU.
8 | EFEnable | On | YES | CxOvrd,OpsOvrd | YES | Exhaust Fan Enable Status | Use this when there is only one exhaust fan associated with AHU.
7 | EFFault | Normal | YES |  | YES | Exhaust Fan Fault Status | Use this when there is only one exhaust fan associated with AHU.
7 | EFSpeed | 15% | YES |  | YES | Exhaust Fan Speed Feedback | Use this when there is only one exhaust fan associated with AHU.
10 | EFSpeedCmd | 15% | YES | CxOvrd,OpsOvrd | YES | Exhaust Fan Speed Cmd | Use this when there is only one exhaust fan associated with AHU.
15 | EFStackVelocity | 0 ft/min | YES |  | YES | Exhaust Stack Velocity | Use this when there is only one exhaust fan associated with AHU.
8 | EFStatus | Running | YES |  | YES | Exhaust Fan Status | Use this when there is only one exhaust fan associated with AHU.
12 | EF1EnableCmd | On | YES | CxOvrd,OpsOvrd | YES | EF-1 Exhaust Fan Enable Cmd | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
9 | EF1Enable | On | YES | CxOvrd,OpsOvrd | YES | EF-1 Exhaust Fan Enable Status | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
8 | EF1Fault | Normal | YES |  | YES | EF-1 Exhaust Fan Fault Status | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
8 | EF1Speed | 15% | YES |  | YES | EF-1 Exhaust Fan Speed Feedback | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
11 | EF1SpeedCmd | 15% | YES | CxOvrd,OpsOvrd | YES | EF-1 Exhaust Fan Speed Cmd | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
16 | EF1StackVelocity | 0 ft/min | YES |  | YES | EF-1 Exhaust Stack Velocity | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
9 | EF1Status | Running | YES |  | YES | EF-1 Exhaust Fan Status | Use this convention if there is more than one exhaust fan. "EF1" is example. Refer to the exhaust fan by its simplifed schedule tag (e.g. EF1, EF2, etc.)
8 | EFVFDPwr | 7.0 kW | YES |  |  | Exhaust Fan VFD Power
13 | EFVFDSpdMinSp | 15% |  | CxOvrd,OpsOvrd | YES | Exhaust Fan VFD Speed Min Setpoint
13 | EFVFDStatus_1 | FALSE | YES |  | YES | EF-1 Exhaust Fan VFD Fault Status
9 | ExhStatLp | 0.631 |  |  |  | Exhaust Air Static Pressure Control - Signal Output
82 | NOTE: NEED TO ADD POINTS RELATED TO LEAD/LAG and STAGING OF EXHAUST FANS (8/22/18)

## 4b-AHU DualDuct (hidden)
StandardName | Example_Value | TrendLocally | OverrideAbility | IncldOnGraphic | Full Name | Additional Description
PLACEHOLDER FOR FUTURE DEVELOPMENT

## 6-BldgWaterLoops (hidden)
StandardName | Example_Value | TrendLocally | OverrideAbility | IncldOnGraphic | Full Name | Additional Description
PLACEHOLDER FOR FUTURE DEVELOPMENT